## RFI Log
Ironwood Point Data Center — Building A, Phase 1
Request for Information (RFI) Log ¦ Project No. MDC-2026-0417 ¦ Updated 06/30/2026
RFI No. | Date Issued | Spec Section / Drawing Ref. | Subject | Question | Submitted By | Status | Date Closed / Response
RFI-014 | 2026-06-05 | 26 33 53 / E-501 | UPS battery autonomy basis | Spec Section 26 33 53 requires 15 minutes of battery autonomy at full rated load. Please confirm whether the 15-minute autonomy is based on the UPS system's 500 kW module rating or the actual coincident critical IT load (currently estimated at 420 kW per the Basis of Design). This affects battery string sizing and cabinet count. | Halvorsen & Pratt Engineering | Closed | 2026-06-12 — EOR confirmed 15 min autonomy is based on the full 500 kW nameplate rating of each UPS module, not the coincident IT load, to preserve growth capacity per Basis of Design Sec. 3.4.
RFI-015 | 2026-06-18 | 26 33 53 | Eaton 93PM proposed as approved equal | Contractor (Apex Critical Power Solutions) has proposed the Eaton 93PM as an approved-equal alternate to the Schneider Galaxy VX basis-of-design unit per Submittal 26 33 53-01. Please confirm this substitution is acceptable for bid/procurement purposes pending full technical review of the submittal. | Apex Critical Power Solutions | Closed | 2026-06-20 — EOR: Eaton 93PM is an acceptable manufacturer per Spec 2.1.A (named approved equal). Full compliance with performance criteria in Part 2 remains subject to submittal review; see Submittal 26 33 53-01.
RFI-016 | 2026-06-27 | 26 33 53 / Submittal 26 33 53-01 | UPS battery autonomy discrepancy | Submittal 26 33 53-01 (Eaton 93PM) states battery autonomy of 10 minutes at full rated load; battery calculation in Appendix C is based on a 10-minute string configuration. Specification Section 26 33 53, Art. 2.2 requires a minimum of 15 minutes autonomy at full rated load. Please confirm whether Contractor is to (a) revise the battery string sizing to meet the 15-minute requirement, or (b) submit a formal request for reduced autonomy with supporting analysis. | Halvorsen & Pratt Engineering | Open
RFI-017 | 2026-06-27 | 26 33 53 / Submittal 26 33 53-01 | UPS efficiency below specified minimum | Submittal 26 33 53-01 lists overall AC-AC efficiency of 96.2% in double-conversion mode. Specification Section 26 33 53, Art. 2.2 requires minimum 97.0% efficiency at 40-100% load. Please clarify whether the submitted factory efficiency curve (Appendix B) reflects a different operating condition than specified, or whether Contractor is requesting a deviation from the specified minimum. Note potential impact to mechanical cooling load and UPS room heat rejection calculations if 96.2% is carried forward. | Halvorsen & Pratt Engineering | Open
RFI-018 | 2026-07-01 | 26 24 13 / 26 33 53 | UPS output breaker coordination with switchboard SWBD-A1 | Requesting confirmation that the UPS system's integral output breaker and the upstream feeder breaker at SWBD-A1 have been coordinated per the project's protective device coordination study (Section 26 05 73). Submittal 26 33 53-01 does not include breaker trip settings. | Ironwood Electrical Contractors | Open