PROJECT MANUAL

SECTION 26 33 53

STATIC UNINTERRUPTIBLE POWER SUPPLY (UPS) SYSTEM

Ironwood Point Data Center — Building A, Phase 1

Meridian Data Centers, LLC  |  Project No. MDC-2026-0417  |  Issued for Construction  |  Rev. 2 — 06/12/2026

# PART 1 — GENERAL

## 1.1  SUMMARY

A. This Section specifies modular, double-conversion (VFI, per IEC 62040-3) static uninterruptible power supply (UPS) systems, associated battery energy storage, and factory-integrated distribution for the Building A data hall critical power chain.

B. Section Includes:

- UPS power modules and system cabinet(s), configured N+1 within each system

- Valve-regulated lead-acid (VRLA) battery cabinets and battery monitoring system (BMS)

- Integral maintenance bypass and output distribution

- Remote monitoring, building management system (BMS/BAS) integration, and network management card

- Factory witness testing, startup, and commissioning support

C. Related Sections: 26 24 13 (Switchboards), 26 24 16 (Panelboards), 26 36 00 (Automatic Transfer Switches), 27 05 00 (DCIM / SCADA Integration).

## 1.2  REFERENCES

- IEC 62040-1 — UPS Safety Requirements

- IEC 62040-2 — UPS EMC Requirements

- IEC 62040-3 — UPS Method of Specifying Performance and Test Requirements (VFI classification)

- UL 1778 — Standard for Uninterruptible Power Systems

- NFPA 70 (NEC) — Article 645, Article 480 (Storage Batteries)

- IEEE 1100 (Emerald Book) — Powering and Grounding Electronic Equipment

- Uptime Institute Tier III — Concurrently Maintainable Site Infrastructure (basis of design)

## 1.3  SUBMITTALS

A. Product Data: Manufacturer's catalog data, nameplate ratings, dimensioned drawings, weight, and heat rejection (BTU/hr) for each UPS module and battery cabinet.

B. Shop Drawings: Single-line diagrams, front/rear elevations, conduit entry locations, and floor loading data.

C. Battery Calculations: Manufacturer's battery sizing calculation demonstrating compliance with the autonomy time specified in Part 2 at the stated load and end-of-discharge voltage, per IEEE 485.

D. Test Reports: Factory witness test (FWT) report and, where applicable, third-party certification (UL/CSA/ETL) for the specific model submitted.

E. O&M Manuals and as-built single-line diagrams at Substantial Completion.

## 1.4  QUALITY ASSURANCE

A. Manufacturer Qualifications: Minimum 10 years documented experience manufacturing UPS equipment of the type and capacity specified, with a factory-authorized service organization within 100 miles of the Site capable of 4-hour emergency response.

B. All equipment furnished under this Section shall be new, of current production, and listed by a Nationally Recognized Testing Laboratory (NRTL).

## 1.5  WARRANTY

A. Manufacturer's standard parts and labor warranty: minimum 2 years from Substantial Completion, extendable to 5 years via service agreement.

B. Battery warranty: minimum 3 years full replacement, prorated to year 7, per manufacturer's published warranty schedule.

# PART 2 — PRODUCTS

## 2.1  MANUFACTURERS

A. Basis of Design: Schneider Electric Galaxy VX, or approved equal by Eaton (93PM) or Vertiv (Liebert EXL S1).

B. Substitutions: Requests for substitution shall be submitted in accordance with Section 01 25 00 and demonstrate compliance with all performance criteria of Part 2 herein; partial compliance is not acceptable without Engineer's written approval.

## 2.2  SYSTEM CONFIGURATION AND RATINGS

| Parameter | Requirement |
| --- | --- |
| System Topology | Double conversion, on-line (VFI-SS-111 per IEC 62040-3) |
| Rated Capacity (per module) | 500 kVA / 500 kW at unity output power factor |
| System Redundancy | N+1 modular configuration, minimum 2 modules per frame, hot-swappable |
| Input Voltage / Phase | 480 VAC, 3-phase, 3-wire + ground, 60 Hz |
| Output Voltage / Phase | 480 VAC, 3-phase, 3-wire + ground, 60 Hz, ±1% |
| Input Frequency Range | 60 Hz ±5%, walk-in on restoration |
| Input Current Total Harmonic Distortion (THDi) | < 5% at full rated linear load, without input filter |
| Output Voltage THD | < 2% linear load, < 5% non-linear load |
| Overall AC-AC Efficiency (Double Conversion Mode) | ≥ 97.0% at 40–100% load |
| ECO / High-Efficiency Mode Efficiency | ≥ 99.0% (available; not enabled for Tier III operation without Owner approval) |
| Overload Capacity | 125% for 10 minutes; 150% for 1 minute |
| Battery Backup / Autonomy | 15 minutes minimum at full rated load (500 kW), new battery, 25°C, to end-of-discharge voltage |
| Battery Type | Valve-regulated lead-acid (VRLA), sealed, telecom-grade, front-access, seismic-rated rack |
| Parallel Capability | Up to 6 modules in parallel via factory system bus, no single point of failure |
| Acoustic Noise | ≤ 72 dBA at 1 meter, full load |
| Operating Temperature Range | 0°C to 40°C (32°F to 104°F) |
| Operating Relative Humidity | 0–95% non-condensing |
| Altitude (no derate) | Up to 1,000 m (3,300 ft) |
| Enclosure Rating | NEMA 1 / IP20 minimum, front and rear service access |
| Ground Fault / Insulation Monitoring | Integral, per NEC Article 250 and Article 645 |

## 2.3  MONITORING AND COMMUNICATIONS

- Front panel: graphical touchscreen LCD/LED display of all operating parameters and alarms.

- Network Management Card (NMC): SNMP v2/v3, Modbus TCP, and BACnet/IP gateway for BMS integration.

- Dry contact interface: minimum 8 programmable form-C relay outputs for critical alarms.

- Battery Monitoring System (BMS): per-string voltage, temperature, and internal impedance/conductance trending with predictive end-of-life alarming.

- Remote Emergency Power Off (REPO): hardwired, normally-closed loop, coordinated with fire alarm system per NFPA 70/NEC 645.10.

## 2.4  MAINTENANCE BYPASS

A. Provide an integral, key-interlocked make-before-break maintenance bypass cabinet permitting complete isolation and de-energization of the UPS module(s) for service without interrupting power to the critical load.

B. Bypass switch shall be rated for continuous duty at 125% of the UPS module's rated output current.

# PART 3 — EXECUTION

## 3.1  INSTALLATION

A. Install UPS and battery cabinets level, plumb, and anchored per manufacturer's seismic bracing details for the project's assigned Seismic Design Category.

B. Maintain manufacturer's minimum clearances for front, rear, and side service access; coordinate with data hall hot/cold aisle containment layout.

C. Provide dedicated equipment grounding conductor sized per NEC Table 250.122, bonded to the building's signal reference grid.

## 3.2  FIELD QUALITY CONTROL

A. Startup: Performed by manufacturer's factory-authorized technician. Submit startup report prior to scheduling integrated systems testing (IST).

B. Testing: Full-load bank test (resistive load bank) to verify rated capacity, efficiency, and battery autonomy match the values submitted under Article 1.3.C, witnessed by Owner's Representative and Commissioning Agent.

C. Integrated Systems Test (IST): UPS shall be exercised through simulated utility loss, battery discharge, generator start/transfer, and bypass transfer scenarios per the project's Level 5 commissioning plan.

## 3.3  TRAINING

A. Provide minimum 8 hours of on-site operations and maintenance training for Owner's facilities staff, including battery maintenance and emergency bypass procedures.

— END OF SECTION 26 33 53 —